## Normal Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt16 | CT_0 current | Unit 0.1A. The value 0 ~ 65535 indicates 0 ~ 6553.5 A.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17 | 03, 04 | R | Uint16 | CT_1 current
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | CT_2 current
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint16 | CT_3 current
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A | 03, 04 | R | Uint16 | CT_4 current
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | CT_5 current
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_0 | Bit 15 (MSB): Unit Control Bit If this bit is 0, the unit is 1W. The bit 1 indicates the unit is 100W. Bit 0 ~ Bit 14: The value of instantaneous power When the Bit 15 is 0, the value 0 ~ 32767 indicates 0 ~ 32767W. If the Bit 15 is 1, the value 0 ~ 32767 indicates 0 ~ 3267600 W. This value is the absolute value of instantaneous power which is not affected by the CT direction.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_1
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_2
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_3
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20 | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_4
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_5
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint16 | Energy calculated by CT_0 | Unit kWh. The value 0 ~ 65535 indicates 0 ~ 65535 kWh. This value is the absolute value of energy which is not affected by the CT direction.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23 | 03, 04 | R | Uint16 | Energy calculated by CT_1
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Energy calculated by CT_2
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint16 | Energy calculated by CT_3
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26 | 03, 04 | R | Uint16 | Energy calculated by CT_4
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Energy calculated by CT_5
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint16 | Power factor calculated by CT_0 | The value -10000 ~ 10000 indicates -1.0000 ~ 1.0000. If the 'ignore the CT direction' (default) is configured, this value is obtained by taking the absolute value of power factor to each phase. In the case of following the CT direction, it is obtained a negative value if the CT direction is opposite of the direction of the cable current.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29 | 03, 04 | R | Uint16 | Voltage | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V.
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | 03, 04 | R | Uint16 | [High byte] Timestamp: Year | The value 0 ~ 99 indicates A.D. 2000 ~ 2099.
[11 empty] | [Low byte] Timestamp: Month | The value 1 ~ 12 indicates January ~ December.
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B | 03, 04 | R | Uint16 | [High byte] Timestamp: Day | The value 1 ~ 31 indicates 1st ~ 31th of the month.
[11 empty] | [Low byte] Timestamp: Hour | The value 0 ~ 23 indicates 0 AM ~ 11 PM.
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C | 03, 04 | R | Uint16 | [High byte] Timestamp: Minute | The value 0 ~ 59 indicates 0 ~ 59 minutes of a hour.
[11 empty] | [Low byte] Timestamp: Second | The value 0 ~ 59 indicates 0 ~ 59 seconds of a minute.
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D | - | - | - | - | -
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## C-PF-V Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16) | C
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt16 | CT_0 current | Unit 0.1A. The value 0 ~ 65535 indicates 0 ~ 6553.5 A.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17 | 03, 04 | R | Uint16 | CT_1 current
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | CT_2 current
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint16 | CT_3 current
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A | 03, 04 | R | Uint16 | CT_4 current
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | CT_5 current
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | int16 | Power factor calculated by CT_0 | The value -10000 ~ 10000 indicates -1.0000 ~ 1.0000. If the 'ignore the CT direction' (default) is configured, this value is obtained by taking the absolute value of power factor to each phase. In the case of following the CT direction, it is obtained a negative value if the CT direction is opposite of the direction of the cable current.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D | 03, 04 | R | int16 | Power factor calculated by CT_1
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | int16 | Power factor calculated by CT_2
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | int16 | Power factor calculated by CT_3
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20 | 03, 04 | R | int16 | Power factor calculated by CT_4
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | int16 | Power factor calculated by CT_5
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint16 | Voltage used by CT_0 | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23 | 03, 04 | R | Uint16 | Voltage used by CT_1
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Voltage used by CT_2
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint16 | Voltage used by CT_3
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26 | 03, 04 | R | Uint16 | Voltage used by CT_4
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Voltage used by CT_5
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint16 | [High byte] Timestamp: Year | The value 0 ~ 99 indicates A.D. 2000 ~ 2099.
[11 empty] | [Low byte] Timestamp: Month | The value 1 ~ 12 indicates January ~ December.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29 | 03, 04 | R | Uint16 | [High byte] Timestamp: Day | The value 1 ~ 31 indicates 1st ~ 31th of the month.
[11 empty] | [Low byte] Timestamp: Hour | The value 0 ~ 23 indicates 0 AM ~ 11 PM.
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | 03, 04 | R | Uint16 | [High byte] Timestamp: Minute | The value 0 ~ 59 indicates 0 ~ 59 minutes of a hour.
[11 empty] | [Low byte] Timestamp: Second | The value 0 ~ 59 indicates 0 ~ 59 seconds of a minute.
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B | - | - | - | - | -
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## P-Wh Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt16 | Instantaneous power calculated by CT_0 | Bit 15 (MSB): Unit Control Bit If this bit is 0, the unit is 1W. The bit 1 indicates the unit is 100W. Bit 0 ~ Bit 14: The value of instantaneous power When the Bit 15 is 0, the value 0 ~ 32767 indicates 0 ~ 32767W. If the Bit 15 is 1, the value 0 ~ 32767 indicates 0 ~ 3267600 W. This value is the absolute value of instantaneous power which is not affected by the CT direction.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17 | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_1
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_2
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_3
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_4
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | Instantaneous power calculated by CT_5
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint16 | High precision energy calculated by CT_0 | Unit 0.1Wh. The value 0 ~ 10000 indicates 0 ~ 1 kWh. This value is the absolute value of energy which is not affected by the CT direction. This value is the decimal par of the corresponding energy, and is used to understand the status of the energy accumulation while appling in the small current or voltage.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D | 03, 04 | R | Uint16 | High precision energy calculated by CT_1
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | High precision energy calculated by CT_2
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint16 | High precision energy calculated by CT_3
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20 | 03, 04 | R | Uint16 | High precision energy calculated by CT_4
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | High precision energy calculated by CT_5
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint16 | [High byte] Timestamp: Year | The value 0 ~ 99 indicates A.D. 2000 ~ 2099.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23 |  |  |  | [Low byte] Timestamp: Month | The value 1 ~ 12 indicates January ~ December.
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | [High byte] Timestamp: Day | The value 1 ~ 31 indicates 1st ~ 31th of the month.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 |  |  |  | [Low byte] Timestamp: Hour | The value 0 ~ 23 indicates 0 AM ~ 11 PM.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26 | 03, 04 | R | Uint16 | [High byte] Timestamp: Minute | The value 0 ~ 59 indicates 0 ~ 59 minutes of a hour.
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 |  |  |  | [Low byte] Timestamp: Second | The value 0 ~ 59 indicates 0 ~ 59 seconds of a minute.
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | - | - | - | - | -
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## Engineer Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt16 | Loop No. | The value range 0 ~ 2 presents where the following data are obtained from. The value 0 indicates the data comes from CT_0 and CT_3. The value 1 indicates the data comes from CT_1 and CT_4. The value 2 indicates the data comes from CT_2 and CT_5.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17 | 03, 04 | R | Uint16 | Current of the 1st set | Unit 0.1A. The value 0 ~ 65535 indicates 0 ~ 6553.5 A. The Loop No. 0 indicates this value to CT_0. The Loop No. 1 and 2 indicate the value to CT_1 and CT_2 respectively.
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | Current total harmonic distortion of the 1st set | The value 0 ~ 39999 presents 0% ~ 399.99% current total harmonic distortion. The value 0% indicates there is no harmonic part in the source current. The Loop No. 0 indicates this value to CT_0. The Loop No. 1 and 2 indicate the values to CT_1 and CT_2 respectively.
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint16 | Instantaneous powe of the 1st set | Bit 15 (MSB): Unit Control Bit If this bit is 0, the unit is 1W. The bit 1 indicates the unit is 100W. Bit 0 ~ Bit 14: The value of instantaneous power When the Bit 15 is 0, the value 0 ~ 32767 indicates 0 ~ 32767W. If the Bit 15 is 1, the value 0 ~ 32767 indicates 0 ~ 3267600 W. This value is the absolute value of instantaneous power which is not affected by the CT direction. The Loop No. 0, 1 and 2 indicates the values to CT_0, CT_1 and CT_2 respectively.
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A | 03, 04 | R | Uint16 | Energy of the 1st set | Unit kWh. The value 0 ~ 65535 indicates 0 ~ 65535kWh. This value is the absolute value of energy which is not affected by the CT direction, and is used to understand the status of the energy accumulation while appling in the small current or voltage. The Loop No. 0, 1 and 2 indicates the values to CT_0, CT_1 and CT_2 respectively.
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | int16 | Power factor of the 1st set | The value -10000 ~ 10000 indicates -1.0000 ~ 1.0000. If the 'ignore the CT direction' (default) is configured, this value is obtained by taking the absolute value of power factor to each phase. In the case of following the CT direction, it is obtained a negative value if the CT direction is opposite of the direction of the cable current. The Loop No. 0, 1 and 2 indicates the values to CT_0, CT_1 and CT_2 respectively.
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint16 | Current of the 2nd set | Unit 0.1A. The value 0 ~ 65535 indicates 0 ~ 6553.5 A. The Loop No. 0 indicates this value to CT_3. The Loop No. 1 and 2 indicate the value to CT_4 and CT_5 respectively.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D | 03, 04 | R | Uint16 | Current total harmonic distortion of the 2nd set | The value 0 ~ 39999 presents 0% ~ 399.99% current total harmonic distortion. The value 0% indicates there is no harmonic part in the source current. The Loop No. 0 indicates this value to CT_3. The Loop No. 1 and 2 indicate the values to CT_4 and CT_5 respectively.
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Instantaneous powe of the 2nd set | Bit 15 (MSB): Unit Control Bit If this bit is 0, the unit is 1W. The bit 1 indicates the unit is 100W. Bit 0 ~ Bit 14: The value of instantaneous power When the Bit 15 is 0, the value 0 ~ 32767 indicates 0 ~ 32767W. If the Bit 15 is 1, the value 0 ~ 32767 indicates 0 ~ 3267600 W. This value is the absolute value of instantaneous power which is not affected by the CT direction. The Loop No. 0, 1 and 2 indicates the values to CT_3, CT_4 and CT_5 respectively.
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint16 | Energy of the 2nd set | Unit kWh. The value 0 ~ 65535 indicates 0 ~ 65535kWh. This value is the absolute value of energy which is not affected by the CT direction, and is used to understand the status of the energy accumulation while appling in the small current or voltage. The Loop No. 0, 1 and 2 indicates the values to CT_3, CT_4 and CT_5 respectively.
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20 | 03, 04 | R | int16 | Power factor of the 2nd set | The value -10000 ~ 10000 indicates -1.0000 ~ 1.0000. If the 'ignore the CT direction' (default) is configured, this value is obtained by taking the absolute value of power factor to each phase. In the case of following the CT direction, it is obtained a negative value if the CT direction is opposite of the direction of the cable current. The Loop No. 0, 1 and 2 indicates the values to CT_3, CT_4 and CT_5 respectively.
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Phase voltage | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. In the 3 Phase 3 Wire 3 CT setting, this value will be the product of the phase voltage and 1.732.
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint16 | Voltage total harmonic distortion | The value 0 ~ 39999 presents 0% ~ 399.99% voltage total harmonic distortion. The value 0% indicates there is no harmonic part in the source voltage.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23 | 03, 04 | R | Uint16 | [High byte] Timestamp: Year | The value 0 ~ 99 indicates A.D. 2000 ~ 2099.
[11 empty] | [Low byte] Timestamp: Month | The value 1 ~ 12 indicates January ~ December.
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | [High byte] Timestamp: Day | The value 1 ~ 31 indicates 1st ~ 31th of the month.
[11 empty] | [Low byte] Timestamp: Hour | The value 0 ~ 23 indicates 0 AM ~ 11 PM.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint16 | [High byte] Timestamp: Minute | The value 0 ~ 59 indicates 0 ~ 59 minutes of a hour.
[11 empty] | [Low byte] Timestamp: Second | The value 0 ~ 59 indicates 0 ~ 59 seconds of a minute.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26 | - | - | - | - | -
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## V-drop 1 Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt32 | Date of 1st (newest) voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | Lowest voltage of 1st (newest) voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint32 | Date of 2nd voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | Lowest voltage of 2nd voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint32 | Date of 3rd voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Lowest voltage of 3rd voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint32 | Date of 4th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Lowest voltage of 4th voltage drop | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint32 | Date of 5th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Lowest voltage of 5th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint32 | Date of 6th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Lowest voltage of 6th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint32 | Date of 7th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | 03, 04 | R | Uint16 | Lowest voltage of 7th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B | - | - | - | - | -
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## V-drop 2 Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt32 | Date of 8th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | Lowest voltage of 8th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint32 | Date of 9th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | Lowest voltage of 9th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint32 | Date of 10th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Lowest voltage of 10th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint32 | Date of 11th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Lowest voltage of 11th voltage drop | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint32 | Date of 12th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Lowest voltage of 12th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint32 | Date of 13th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Lowest voltage of 13th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint32 | Date of 14th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | 03, 04 | R | Uint16 | Lowest voltage of 14th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B | - | - | - | - | -
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## V-drop 3 Mode Single Phase
Keyin the Node ID |  |  |  | Note: (1) The Node ID must be 1 ~ 31. (2)The maximum allowed data length for one Modbus command of iWSN-200U is 72 words (Uint16/int16) (3) The maximum allowed data length for one Modbus command of iWSN-200E is 125 words (Uint16/int16)
1 | [7 empty] | iWSN-9603 series modules The different working mode must use corresponding Modbus mapping table. Please refer to the following red words for detail.
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | R/W | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Auto-response period of sensor module. | (Bit7~Bit6) '00' indicates the unit of the value Bit0~Bit5 is second. '01' indicates the unit of the value Bit0~Bit5 is minute. '10' indicates the unit of the value Bit0~Bit5 is hour. '11' is reserved. (Bit5~Bit0) The time period which is depend on the unit decided by the Bit7 and Bit6. The value ranges 1 ~ 63, and 0 is reserved. For example, if the value of Bit7 ~ Bit6 is 00 and the value of Bit5 ~ Bit0 is 10, it indicates the Auto-response period is 10 seconds.
[11 empty] | [Low byte] The received signal strength of iWSN-200 series. | The value ranges 0~255. The bigger of the value indicates the better radio signal strength. The value over 120 is recommended to get good communication quality.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] Firmware version | The value ranges 10~255. For example, value 10 indicates v1.00, and 254 indicates v25.40.
[11 empty] | [Low byte] Wireless packrage information. | Bit 7: Reserved. Bit 6: Expansion Format Bit. If the setting command uses subfunction code, the bit is 1. Bit 5: Error Response Bit. If the configuration command has some errors, the bit is 1. Bit 4: Time Sync Bit. When the time sync package is received by the sensor module, this bit is changed to 1. It will be changed to 0 automatically if there is no other time sync package received in 3 minutes. Bit 0 ~ Bit 3: The serial No of package. The value ranges 0 ~ 15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] Sensor Module Code. | The value ranges 0~255. Please refer to sheet 'Sensor Module Code'.
[11 empty] | [Low byte] Expansion Module Code. | The value ranges 0~255. Please refer to sheet 'Expansion Module Code'.
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The start address of the RF package. | Always 0.
[9 empty] | R | Uint16 | [Low byte] Hardware status | Always 2 (0x02): Single Phase 2 Wire.
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | 03, 04 | R | Unt16 | [High byte] Module status 1 | Bit 7: Voltage Frequency. 0 is for 60Hz and 1 is for50Hz。 Bit 6: Reserved. Bit 5: Phase seqeuence. 0 is for clockwise (correct) phase sequence and 1 is for others. Bit 4: CT direction. 0 is for ignore the CT direction. If this bit is 1, the sensor module judges the value of instantaneous power, engrey and power factor negative or positive depending on the direction of the CT direction and cable current. The default is 0. Bit 0 ~ Bit 3: Operation Mode. Different operation modes will get different RF packages which must refer to the corresponding sheet for the Modbus address. Value 0: Normal Mode (default), please refer to 'Normal Mode Single Phase' sheet. Value 1: C-PF-V Mod, please refer to 'C-PF-V Mode Single Phase' sheet. Value 2: P-Wh Mode, please refer to 'P-Whl Mode Single Phase' sheet. Value 3: Engineer Mode, please refer to 'Engineer Mode Single Phase' sheet. Value 4: V-drop 1 Mode, please refer to 'V-drop 1 Mode Single Phase' sheet. Value 5: V-drop 2 Mode, please refer to 'V-drop 2 Mode Single Phase' sheet. Value 6: V-drop 3 Mode, please refer to 'V-drop 3 Mode Single Phase' sheet.
[11 empty] | [Low byte] Module status 2 | Bit 7: Voltage frequency detection mode. 0 (default) is for auto-detection and 1 is for fixed frequency. Bit 6: Auto-response duty selection. 0 (default) is for configuring the duty by DIP switch and 1 is for configuring the duty by software. Bit 5: Voltage drop alarm. 0 is for no alarm and 1 is for alarm happened. When the voltage is over the voltage threshold more than 3 minutes, it will be changed to 0 automatically. Bit 4: Reserved. Bit 3 ~ Bit 0: Error status. Different value indicates different kinds of hardware error. If this value is not 0, please contact to the distributor for help.
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16 | 03, 04 | R | Unt32 | Date of 15th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18 | 03, 04 | R | Uint16 | Lowest voltage of 15th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19 | 03, 04 | R | Uint32 | Date of 16th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | Lowest voltage of 16th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint32 | Date of 17th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Lowest voltage of 17th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint32 | Date of 18th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Lowest voltage of 18th voltage drop | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint32 | Date of 19th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Lowest voltage of 19th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint32 | Date of 20th voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Lowest voltage of 20th voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint32 | Date of 21th (oldest) voltage drop event | Bit 31 ~ Bit 28: the unit digit of the year number. For example, the value 1 indicates 2021. Bit 27 ~ Bit 24: Month. the value 1 ~ 12 presents January ~ December. Bit 23 ~ Bit 18: Day. The value 1 ~ 31 indicates 1st ~ 31th of the month. Bit 17 ~ Bit 12: Hour. The value 0 ~ 23 indicates 0 AM ~ 11 PM. Bit 11 ~ Bit 6: Minute. The value 0 ~ 59 indicates 0 ~ 59 minutes of the hour. Bit 5 ~ Bit 0: Second. The value 0 ~ 59 indicates 0 ~ 59 seconds of the minute.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | 03, 04 | R | Uint16 | Lowest voltage of 21th (oldest) voltage drop event | Unit 0.1V. The value 0 ~ 65535 indicates 0 ~ 6553.5 V. When the voltage keeps lower than the configured threshold throughout the configured time, the voltage drop event is happened. During the event, the logged voltage value will be covered by the detected lower voltage.
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B | - | - | - | - | -
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## Sensor Module Code
Code | Module name | Sensor type | Power supply type | Battery Type | Charging type | Suppot Expansion Module
14 (0x0E) | iWSN-9601-PCT-ME-IP33 iWSN-9601-160-ME-IP33 iWSN-9601-240-ME-IP33 iWSN-9601-360-ME-IP33 | 6 Split CT (CT Option) 6 Split Core 100 A CT 6 Split Core 200 A CT 6 Split Core 400 A CT | AC power | - | - | No

## Expansion Module Code
Code | Module name | Type | Support Module
255 (0xFF) | No expansion module connected | - | -

## iWSN Sensor資料_機台差異測試用(100ms) (hidden)
↓輸入站號1~15可計算資料位址
Sensor 站號
1
|  |  |  | Sensor型號 |  |  |  |  | Sensor型號
|  |  |  | 1V6C (24 words) |  |  |  |  | 1V6C (10 words)
Base1 位址 (Dec) | Base1 位址 (Dec) | Base0 位址 (Dec) | Base0 位址 (Hex) | 命令碼 | 屬性 | 資料型態 | 說明 | 備註 | 命令碼 | 屬性 | 資料型態 | 說明 | 備註
40257 | 30257 | 256 | 100 | 03, 04 | R | Uint16 | 第0筆量測資料 | - | 03, 04 | R | Uint16 | 第0筆量測資料 | -
40258 | 30258 | 257 | 101 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40259 | 30259 | 258 | 102 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40260 | 30260 | 259 | 103 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40261 | 30261 | 260 | 104 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40262 | 30262 | 261 | 105 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40263 | 30263 | 262 | 106 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40264 | 30264 | 263 | 107 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40265 | 30265 | 264 | 108 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40266 | 30266 | 265 | 109 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40267 | 30267 | 266 | 10A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第1筆量測資料 | -
40268 | 30268 | 267 | 10B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40269 | 30269 | 268 | 10C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40270 | 30270 | 269 | 10D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40271 | 30271 | 270 | 10E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40272 | 30272 | 271 | 10F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40273 | 30273 | 272 | 110 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40274 | 30274 | 273 | 111 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40275 | 30275 | 274 | 112 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40276 | 30276 | 275 | 113 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40277 | 30277 | 276 | 114 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第2筆量測資料 | -
40278 | 30278 | 277 | 115 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40279 | 30279 | 278 | 116 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40280 | 30280 | 279 | 117 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40281 | 30281 | 280 | 118 | 03, 04 | R | Uint16 | 第1筆量測資料 | - | 03, 04 | R | Uint16
40282 | 30282 | 281 | 119 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40283 | 30283 | 282 | 11A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40284 | 30284 | 283 | 11B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40285 | 30285 | 284 | 11C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40286 | 30286 | 285 | 11D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40287 | 30287 | 286 | 11E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第3筆量測資料 | -
40288 | 30288 | 287 | 11F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40289 | 30289 | 288 | 120 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40290 | 30290 | 289 | 121 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40291 | 30291 | 290 | 122 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40292 | 30292 | 291 | 123 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40293 | 30293 | 292 | 124 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40294 | 30294 | 293 | 125 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40295 | 30295 | 294 | 126 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40296 | 30296 | 295 | 127 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40297 | 30297 | 296 | 128 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第4筆量測資料 | -
40298 | 30298 | 297 | 129 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40299 | 30299 | 298 | 12A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40300 | 30300 | 299 | 12B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40301 | 30301 | 300 | 12C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40302 | 30302 | 301 | 12D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40303 | 30303 | 302 | 12E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40304 | 30304 | 303 | 12F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40305 | 30305 | 304 | 130 | 03, 04 | R | Uint16 | 第2筆量測資料 | - | 03, 04 | R | Uint16
40306 | 30306 | 305 | 131 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40307 | 30307 | 306 | 132 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第5筆量測資料 | -
40308 | 30308 | 307 | 133 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40309 | 30309 | 308 | 134 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40310 | 30310 | 309 | 135 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40311 | 30311 | 310 | 136 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40312 | 30312 | 311 | 137 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40313 | 30313 | 312 | 138 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40314 | 30314 | 313 | 139 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40315 | 30315 | 314 | 13A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40316 | 30316 | 315 | 13B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40317 | 30317 | 316 | 13C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第6筆量測資料 | -
40318 | 30318 | 317 | 13D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40319 | 30319 | 318 | 13E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40320 | 30320 | 319 | 13F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40321 | 30321 | 320 | 140 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40322 | 30322 | 321 | 141 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40323 | 30323 | 322 | 142 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40324 | 30324 | 323 | 143 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40325 | 30325 | 324 | 144 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40326 | 30326 | 325 | 145 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40327 | 30327 | 326 | 146 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第7筆量測資料 | -
40328 | 30328 | 327 | 147 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40329 | 30329 | 328 | 148 | 03, 04 | R | Uint16 | 第3筆量測資料 | - | 03, 04 | R | Uint16
40330 | 30330 | 329 | 149 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40331 | 30331 | 330 | 14A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40332 | 30332 | 331 | 14B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40333 | 30333 | 332 | 14C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40334 | 30334 | 333 | 14D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40335 | 30335 | 334 | 14E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40336 | 30336 | 335 | 14F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40337 | 30337 | 336 | 150 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第8筆量測資料 | -
40338 | 30338 | 337 | 151 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40339 | 30339 | 338 | 152 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40340 | 30340 | 339 | 153 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40341 | 30341 | 340 | 154 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40342 | 30342 | 341 | 155 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40343 | 30343 | 342 | 156 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40344 | 30344 | 343 | 157 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40345 | 30345 | 344 | 158 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40346 | 30346 | 345 | 159 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40347 | 30347 | 346 | 15A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第9筆量測資料 | -
40348 | 30348 | 347 | 15B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40349 | 30349 | 348 | 15C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40350 | 30350 | 349 | 15D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40351 | 30351 | 350 | 15E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40352 | 30352 | 351 | 15F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40353 | 30353 | 352 | 160 | 03, 04 | R | Uint16 | 第4筆量測資料 | - | 03, 04 | R | Uint16
40354 | 30354 | 353 | 161 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40355 | 30355 | 354 | 162 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40356 | 30356 | 355 | 163 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40357 | 30357 | 356 | 164 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第10筆量測資料 | -
40358 | 30358 | 357 | 165 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40359 | 30359 | 358 | 166 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40360 | 30360 | 359 | 167 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40361 | 30361 | 360 | 168 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40362 | 30362 | 361 | 169 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40363 | 30363 | 362 | 16A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40364 | 30364 | 363 | 16B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40365 | 30365 | 364 | 16C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40366 | 30366 | 365 | 16D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40367 | 30367 | 366 | 16E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第11筆量測資料 | -
40368 | 30368 | 367 | 16F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40369 | 30369 | 368 | 170 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40370 | 30370 | 369 | 171 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40371 | 30371 | 370 | 172 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40372 | 30372 | 371 | 173 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40373 | 30373 | 372 | 174 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40374 | 30374 | 373 | 175 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40375 | 30375 | 374 | 176 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40376 | 30376 | 375 | 177 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40377 | 30377 | 376 | 178 | 03, 04 | R | Uint16 | 第5筆量測資料 | - | 03, 04 | R | Uint16 | 第12筆量測資料 | -
40378 | 30378 | 377 | 179 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40379 | 30379 | 378 | 17A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40380 | 30380 | 379 | 17B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40381 | 30381 | 380 | 17C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40382 | 30382 | 381 | 17D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40383 | 30383 | 382 | 17E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40384 | 30384 | 383 | 17F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40385 | 30385 | 384 | 180 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40386 | 30386 | 385 | 181 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40387 | 30387 | 386 | 182 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第13筆量測資料 | -
40388 | 30388 | 387 | 183 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40389 | 30389 | 388 | 184 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40390 | 30390 | 389 | 185 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40391 | 30391 | 390 | 186 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40392 | 30392 | 391 | 187 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40393 | 30393 | 392 | 188 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40394 | 30394 | 393 | 189 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40395 | 30395 | 394 | 18A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40396 | 30396 | 395 | 18B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40397 | 30397 | 396 | 18C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第14筆量測資料 | -
40398 | 30398 | 397 | 18D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40399 | 30399 | 398 | 18E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40400 | 30400 | 399 | 18F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40401 | 30401 | 400 | 190 | 03, 04 | R | Uint16 | 第6筆量測資料 | - | 03, 04 | R | Uint16
40402 | 30402 | 401 | 191 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40403 | 30403 | 402 | 192 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40404 | 30404 | 403 | 193 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40405 | 30405 | 404 | 194 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40406 | 30406 | 405 | 195 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40407 | 30407 | 406 | 196 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第15筆量測資料 | -
40408 | 30408 | 407 | 197 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40409 | 30409 | 408 | 198 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40410 | 30410 | 409 | 199 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40411 | 30411 | 410 | 19A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40412 | 30412 | 411 | 19B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40413 | 30413 | 412 | 19C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40414 | 30414 | 413 | 19D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40415 | 30415 | 414 | 19E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40416 | 30416 | 415 | 19F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40417 | 30417 | 416 | 1A0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第16筆量測資料 | -
40418 | 30418 | 417 | 1A1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40419 | 30419 | 418 | 1A2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40420 | 30420 | 419 | 1A3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40421 | 30421 | 420 | 1A4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40422 | 30422 | 421 | 1A5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40423 | 30423 | 422 | 1A6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40424 | 30424 | 423 | 1A7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40425 | 30425 | 424 | 1A8 | 03, 04 | R | Uint16 | 第7筆量測資料 | - | 03, 04 | R | Uint16
40426 | 30426 | 425 | 1A9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40427 | 30427 | 426 | 1AA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第17筆量測資料 | -
40428 | 30428 | 427 | 1AB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40429 | 30429 | 428 | 1AC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40430 | 30430 | 429 | 1AD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40431 | 30431 | 430 | 1AE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40432 | 30432 | 431 | 1AF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40433 | 30433 | 432 | 1B0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40434 | 30434 | 433 | 1B1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40435 | 30435 | 434 | 1B2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40436 | 30436 | 435 | 1B3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40437 | 30437 | 436 | 1B4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第18筆量測資料 | -
40438 | 30438 | 437 | 1B5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40439 | 30439 | 438 | 1B6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40440 | 30440 | 439 | 1B7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40441 | 30441 | 440 | 1B8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40442 | 30442 | 441 | 1B9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40443 | 30443 | 442 | 1BA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40444 | 30444 | 443 | 1BB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40445 | 30445 | 444 | 1BC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40446 | 30446 | 445 | 1BD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40447 | 30447 | 446 | 1BE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第19筆量測資料 | -
40448 | 30448 | 447 | 1BF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40449 | 30449 | 448 | 1C0 | 03, 04 | R | Uint16 | 第8筆量測資料 | - | 03, 04 | R | Uint16
40450 | 30450 | 449 | 1C1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40451 | 30451 | 450 | 1C2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40452 | 30452 | 451 | 1C3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40453 | 30453 | 452 | 1C4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40454 | 30454 | 453 | 1C5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40455 | 30455 | 454 | 1C6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40456 | 30456 | 455 | 1C7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40457 | 30457 | 456 | 1C8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | - | -
40458 | 30458 | 457 | 1C9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40459 | 30459 | 458 | 1CA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40460 | 30460 | 459 | 1CB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40461 | 30461 | 460 | 1CC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40462 | 30462 | 461 | 1CD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40463 | 30463 | 462 | 1CE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40464 | 30464 | 463 | 1CF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40465 | 30465 | 464 | 1D0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40466 | 30466 | 465 | 1D1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40467 | 30467 | 466 | 1D2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40468 | 30468 | 467 | 1D3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40469 | 30469 | 468 | 1D4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40470 | 30470 | 469 | 1D5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40471 | 30471 | 470 | 1D6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40472 | 30472 | 471 | 1D7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40473 | 30473 | 472 | 1D8 | 03, 04 | R | Uint16 | 第9筆量測資料 | - | 03, 04 | R | Uint16
40474 | 30474 | 473 | 1D9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40475 | 30475 | 474 | 1DA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40476 | 30476 | 475 | 1DB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40477 | 30477 | 476 | 1DC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40478 | 30478 | 477 | 1DD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40479 | 30479 | 478 | 1DE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40480 | 30480 | 479 | 1DF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40481 | 30481 | 480 | 1E0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40482 | 30482 | 481 | 1E1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40483 | 30483 | 482 | 1E2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40484 | 30484 | 483 | 1E3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40485 | 30485 | 484 | 1E4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40486 | 30486 | 485 | 1E5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40487 | 30487 | 486 | 1E6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40488 | 30488 | 487 | 1E7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40489 | 30489 | 488 | 1E8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40490 | 30490 | 489 | 1E9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40491 | 30491 | 490 | 1EA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40492 | 30492 | 491 | 1EB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40493 | 30493 | 492 | 1EC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40494 | 30494 | 493 | 1ED | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40495 | 30495 | 494 | 1EE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40496 | 30496 | 495 | 1EF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40497 | 30497 | 496 | 1F0 | 03, 04 | R | Uint16 | 第10筆量測資料 | - | 03, 04 | R | Uint16
40498 | 30498 | 497 | 1F1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40499 | 30499 | 498 | 1F2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40500 | 30500 | 499 | 1F3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40501 | 30501 | 500 | 1F4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40502 | 30502 | 501 | 1F5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40503 | 30503 | 502 | 1F6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40504 | 30504 | 503 | 1F7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40505 | 30505 | 504 | 1F8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40506 | 30506 | 505 | 1F9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40507 | 30507 | 506 | 1FA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40508 | 30508 | 507 | 1FB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40509 | 30509 | 508 | 1FC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40510 | 30510 | 509 | 1FD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40511 | 30511 | 510 | 1FE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40512 | 30512 | 511 | 1FF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40513 | 30513 | 512 | 200 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40514 | 30514 | 513 | 201 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40515 | 30515 | 514 | 202 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40516 | 30516 | 515 | 203 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40517 | 30517 | 516 | 204 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40518 | 30518 | 517 | 205 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40519 | 30519 | 518 | 206 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40520 | 30520 | 519 | 207 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40521 | 30521 | 520 | 208 | 03, 04 | R | Uint16 | 第11筆量測資料 | - | 03, 04 | R | Uint16
40522 | 30522 | 521 | 209 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40523 | 30523 | 522 | 20A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40524 | 30524 | 523 | 20B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40525 | 30525 | 524 | 20C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40526 | 30526 | 525 | 20D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40527 | 30527 | 526 | 20E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40528 | 30528 | 527 | 20F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40529 | 30529 | 528 | 210 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40530 | 30530 | 529 | 211 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40531 | 30531 | 530 | 212 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40532 | 30532 | 531 | 213 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40533 | 30533 | 532 | 214 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40534 | 30534 | 533 | 215 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40535 | 30535 | 534 | 216 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40536 | 30536 | 535 | 217 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40537 | 30537 | 536 | 218 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40538 | 30538 | 537 | 219 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40539 | 30539 | 538 | 21A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40540 | 30540 | 539 | 21B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40541 | 30541 | 540 | 21C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40542 | 30542 | 541 | 21D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40543 | 30543 | 542 | 21E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40544 | 30544 | 543 | 21F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40545 | 30545 | 544 | 220 | 03, 04 | R | Uint16 | 第12筆量測資料 | - | 03, 04 | R | Uint16
40546 | 30546 | 545 | 221 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40547 | 30547 | 546 | 222 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40548 | 30548 | 547 | 223 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40549 | 30549 | 548 | 224 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40550 | 30550 | 549 | 225 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40551 | 30551 | 550 | 226 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40552 | 30552 | 551 | 227 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40553 | 30553 | 552 | 228 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40554 | 30554 | 553 | 229 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40555 | 30555 | 554 | 22A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40556 | 30556 | 555 | 22B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40557 | 30557 | 556 | 22C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40558 | 30558 | 557 | 22D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40559 | 30559 | 558 | 22E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40560 | 30560 | 559 | 22F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40561 | 30561 | 560 | 230 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40562 | 30562 | 561 | 231 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40563 | 30563 | 562 | 232 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40564 | 30564 | 563 | 233 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40565 | 30565 | 564 | 234 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40566 | 30566 | 565 | 235 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40567 | 30567 | 566 | 236 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40568 | 30568 | 567 | 237 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40569 | 30569 | 568 | 238 | 03, 04 | R | Uint16 | 第13筆量測資料 | - | 03, 04 | R | Uint16
40570 | 30570 | 569 | 239 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40571 | 30571 | 570 | 23A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40572 | 30572 | 571 | 23B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40573 | 30573 | 572 | 23C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40574 | 30574 | 573 | 23D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40575 | 30575 | 574 | 23E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40576 | 30576 | 575 | 23F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40577 | 30577 | 576 | 240 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40578 | 30578 | 577 | 241 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40579 | 30579 | 578 | 242 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40580 | 30580 | 579 | 243 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40581 | 30581 | 580 | 244 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40582 | 30582 | 581 | 245 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40583 | 30583 | 582 | 246 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40584 | 30584 | 583 | 247 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40585 | 30585 | 584 | 248 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40586 | 30586 | 585 | 249 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40587 | 30587 | 586 | 24A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40588 | 30588 | 587 | 24B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40589 | 30589 | 588 | 24C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40590 | 30590 | 589 | 24D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40591 | 30591 | 590 | 24E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40592 | 30592 | 591 | 24F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40593 | 30593 | 592 | 250 | 03, 04 | R | Uint16 | 第14筆量測資料 | - | 03, 04 | R | Uint16
40594 | 30594 | 593 | 251 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40595 | 30595 | 594 | 252 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40596 | 30596 | 595 | 253 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40597 | 30597 | 596 | 254 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40598 | 30598 | 597 | 255 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40599 | 30599 | 598 | 256 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40600 | 30600 | 599 | 257 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40601 | 30601 | 600 | 258 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40602 | 30602 | 601 | 259 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40603 | 30603 | 602 | 25A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40604 | 30604 | 603 | 25B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40605 | 30605 | 604 | 25C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40606 | 30606 | 605 | 25D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40607 | 30607 | 606 | 25E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40608 | 30608 | 607 | 25F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40609 | 30609 | 608 | 260 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40610 | 30610 | 609 | 261 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40611 | 30611 | 610 | 262 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40612 | 30612 | 611 | 263 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40613 | 30613 | 612 | 264 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40614 | 30614 | 613 | 265 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40615 | 30615 | 614 | 266 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40616 | 30616 | 615 | 267 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40617 | 30617 | 616 | 268 | 03, 04 | R | Uint16 | 第15筆量測資料 | - | 03, 04 | R | Uint16
40618 | 30618 | 617 | 269 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40619 | 30619 | 618 | 26A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40620 | 30620 | 619 | 26B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40621 | 30621 | 620 | 26C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40622 | 30622 | 621 | 26D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40623 | 30623 | 622 | 26E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40624 | 30624 | 623 | 26F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40625 | 30625 | 624 | 270 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40626 | 30626 | 625 | 271 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40627 | 30627 | 626 | 272 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40628 | 30628 | 627 | 273 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40629 | 30629 | 628 | 274 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40630 | 30630 | 629 | 275 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40631 | 30631 | 630 | 276 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40632 | 30632 | 631 | 277 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40633 | 30633 | 632 | 278 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40634 | 30634 | 633 | 279 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40635 | 30635 | 634 | 27A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40636 | 30636 | 635 | 27B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40637 | 30637 | 636 | 27C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40638 | 30638 | 637 | 27D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40639 | 30639 | 638 | 27E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40640 | 30640 | 639 | 27F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40641 | 30641 | 640 | 280 | 03, 04 | R | Uint16 | 第16筆量測資料 | - | 03, 04 | R | Uint16
40642 | 30642 | 641 | 281 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40643 | 30643 | 642 | 282 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40644 | 30644 | 643 | 283 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40645 | 30645 | 644 | 284 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40646 | 30646 | 645 | 285 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40647 | 30647 | 646 | 286 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40648 | 30648 | 647 | 287 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40649 | 30649 | 648 | 288 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40650 | 30650 | 649 | 289 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40651 | 30651 | 650 | 28A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40652 | 30652 | 651 | 28B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40653 | 30653 | 652 | 28C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40654 | 30654 | 653 | 28D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40655 | 30655 | 654 | 28E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40656 | 30656 | 655 | 28F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40657 | 30657 | 656 | 290 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40658 | 30658 | 657 | 291 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40659 | 30659 | 658 | 292 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40660 | 30660 | 659 | 293 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40661 | 30661 | 660 | 294 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40662 | 30662 | 661 | 295 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40663 | 30663 | 662 | 296 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40664 | 30664 | 663 | 297 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40665 | 30665 | 664 | 298 | 03, 04 | R | Uint16 | 第17筆量測資料 | - | 03, 04 | R | Uint16
40666 | 30666 | 665 | 299 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40667 | 30667 | 666 | 29A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40668 | 30668 | 667 | 29B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40669 | 30669 | 668 | 29C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40670 | 30670 | 669 | 29D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40671 | 30671 | 670 | 29E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40672 | 30672 | 671 | 29F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40673 | 30673 | 672 | 2A0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40674 | 30674 | 673 | 2A1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40675 | 30675 | 674 | 2A2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40676 | 30676 | 675 | 2A3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40677 | 30677 | 676 | 2A4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40678 | 30678 | 677 | 2A5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40679 | 30679 | 678 | 2A6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40680 | 30680 | 679 | 2A7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40681 | 30681 | 680 | 2A8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40682 | 30682 | 681 | 2A9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40683 | 30683 | 682 | 2AA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40684 | 30684 | 683 | 2AB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40685 | 30685 | 684 | 2AC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40686 | 30686 | 685 | 2AD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40687 | 30687 | 686 | 2AE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40688 | 30688 | 687 | 2AF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40689 | 30689 | 688 | 2B0 | 03, 04 | R | Uint16 | 第18筆量測資料 | - | 03, 04 | R | Uint16
40690 | 30690 | 689 | 2B1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40691 | 30691 | 690 | 2B2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40692 | 30692 | 691 | 2B3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40693 | 30693 | 692 | 2B4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40694 | 30694 | 693 | 2B5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40695 | 30695 | 694 | 2B6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40696 | 30696 | 695 | 2B7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40697 | 30697 | 696 | 2B8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40698 | 30698 | 697 | 2B9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40699 | 30699 | 698 | 2BA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40700 | 30700 | 699 | 2BB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40701 | 30701 | 700 | 2BC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40702 | 30702 | 701 | 2BD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40703 | 30703 | 702 | 2BE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40704 | 30704 | 703 | 2BF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40705 | 30705 | 704 | 2C0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40706 | 30706 | 705 | 2C1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40707 | 30707 | 706 | 2C2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40708 | 30708 | 707 | 2C3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40709 | 30709 | 708 | 2C4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40710 | 30710 | 709 | 2C5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40711 | 30711 | 710 | 2C6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40712 | 30712 | 711 | 2C7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40713 | 30713 | 712 | 2C8 | 03, 04 | R | Uint16 | 第19筆量測資料 | - | 03, 04 | R | Uint16
40714 | 30714 | 713 | 2C9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40715 | 30715 | 714 | 2CA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40716 | 30716 | 715 | 2CB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40717 | 30717 | 716 | 2CC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40718 | 30718 | 717 | 2CD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40719 | 30719 | 718 | 2CE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40720 | 30720 | 719 | 2CF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40721 | 30721 | 720 | 2D0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40722 | 30722 | 721 | 2D1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40723 | 30723 | 722 | 2D2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40724 | 30724 | 723 | 2D3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40725 | 30725 | 724 | 2D4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40726 | 30726 | 725 | 2D5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40727 | 30727 | 726 | 2D6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40728 | 30728 | 727 | 2D7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40729 | 30729 | 728 | 2D8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40730 | 30730 | 729 | 2D9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40731 | 30731 | 730 | 2DA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40732 | 30732 | 731 | 2DB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40733 | 30733 | 732 | 2DC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40734 | 30734 | 733 | 2DD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40735 | 30735 | 734 | 2DE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40736 | 30736 | 735 | 2DF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40737 | 30737 | 736 | 2E0 | 03, 04 | R | Uint16 | 當前封包存放之索引值 | - | 03, 04 | R | Uint16 | 當前封包存放之索引值 | -
40738 | 30738 | 737 | 2E1 | 03, 04 | R | Uint16 | 當前封包存放之起始位址 | - | 03, 04 | R | Uint16 | 當前封包存放之起始位址 | -
40739 | 30739 | 738 | 2E2 | 03, 04 | R | Uint16 | 當前封包存放在FRAM之起始位址 | - | 03, 04 | R | Uint16 | 當前封包存放在FRAM之起始位址 | -