## Data of iWSN sensor
↓Keyin the Node ID 1~31 to calculate the address
Node ID of iWSN Sensor | Note: (1) The maximum length of data that can be polled for each command of iWSN-200U is 72 words (Uint16/int16) (2) The maximum length of data that can be polled for each command of iWSN-200E is 125 words (Uint16/int16)
1
Module name
iWSN-100X / iWSN-101X
iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base1, Dec) | iWSN-200U / iWSN-200R (Base0, Dec) | iWSN-200U / iWSN-200R (Base0, Hex) | iWSN-200E (Base1, Dec) | iWSN-200E (Base1, Dec) | iWSN-200E (Base0, Dec) | iWSN-200E (Base0, Hex) | Function code | Property | Data type | Description | Remarks
40322 | 30322 | 321 | 141 | 40008 | 30008 | 7 | 7 | - | - | - | - | -
40323 | 30323 | 322 | 142 | 40009 | 30009 | 8 | 8
40324 | 30324 | 323 | 143 | 40010 | 30010 | 9 | 9
40325 | 30325 | 324 | 144 | 40011 | 30011 | 10 | A
40326 | 30326 | 325 | 145 | 40012 | 30012 | 11 | B
40327 | 30327 | 326 | 146 | 40013 | 30013 | 12 | C
40328 | 30328 | 327 | 147 | 40014 | 30014 | 13 | D
40329 | 30329 | 328 | 148 | 40015 | 30015 | 14 | E
40330 | 30330 | 329 | 149 | 40016 | 30016 | 15 | F
40331 | 30331 | 330 | 14A | 40017 | 30017 | 16 | 10 | - | - | - | - | -
[8 empty] | - | - | - | - | -
40332 | 30332 | 331 | 14B | 40018 | 30018 | 17 | 11 | 03, 04 | R | Uint16 | [High byte] Automatic response time period of iWSN sensor. | (Bit7~Bit6) 00: Bit0~Bit5 mean the unit is second. 01: Bit0~Bit5 mean the unit is minute. 10: Bit0~Bit5 mean the unit is hour. 11: Reserved. (Bit5~Bit0) Refer the unit of Bit7 and Bit6 to define the time scale. Value 1 to 63: Mean 1~63 unit of time. Value 0: Reserved.
[11 empty] | [Low byte] The receiving signal strength of iWSN-200 series. | The value range is 0~255, the larger the value, the better the signal, and it is recommended to be at least 120 or more.
40333 | 30333 | 332 | 14C | 40019 | 30019 | 18 | 12 | 03, 04 | R | Uint16 | [High byte] The firmware version of iWSN sensor. | Value ranges 10~255. Ex: value 10 = v1.00, value 254 = v25.40.
[11 empty] | [Low byte] The serial number of wireless package. | [High nibble] Reserved.
[Low nibble] The serial number of the wireless packet, the value range is 0~15.
40334 | 30334 | 333 | 14D | 40020 | 30020 | 19 | 13 | 03, 04 | R | Uint16 | [High byte] The module code of iWSN sensor. | Value ranges 0~255. Please refer to the worksheet "Sensor Module Code".
[11 empty] | [Low byte] The module code of extension module. | The value range is 0~255. Please refer to the worksheet "Expansion Module Code".
40335 | 30335 | 334 | 14E | 40021 | 30021 | 20 | 14 | 03, 04 | R | Uint16 | [High byte] The data length of raw data section in the wireless packet. | The value range is 0~48, unit: bytes. Value 0: No wireless packet has been received.
[11 empty] | [Low byte] The percent of battery power. | The value is mean percent (%).
40336 | 30336 | 335 | 14F | 40022 | 30022 | 21 | 15 | - | - | - | - | -
40337 | 30337 | 336 | 150 | 40023 | 30023 | 22 | 16
40338 | 30338 | 337 | 151 | 40024 | 30024 | 23 | 17
40339 | 30339 | 338 | 152 | 40025 | 30025 | 24 | 18
40340 | 30340 | 339 | 153 | 40026 | 30026 | 25 | 19
40341 | 30341 | 340 | 154 | 40027 | 30027 | 26 | 1A | 03, 04 | R | Uint16 | The temperature of thermistor. [Note] For iWSN-101X using. | The value divided by 10 is ℃, and the measurement range is 0℃~+80℃.
40342 | 30342 | 341 | 155 | 40028 | 30028 | 27 | 1B | 03, 04 | R | Uint16 | CO2 concentration. [Note] Use with expansion module iXN-0VC. | The value is ppm, and measuring range: 400 ppm to 60000 ppm.
40343 | 30343 | 342 | 156 | 40029 | 30029 | 28 | 1C | 03, 04 | R | Uint16 | TVOC concentration. [Note] Use with expansion module iXN-0VC. | The value is ppb, and measuring range: 0 ppb to 60000 ppb.
40344 | 30344 | 343 | 157 | 40030 | 30030 | 29 | 1D | 03, 04 | R | Uint16 | Environment temperature. [Note] Use with expansion module iXN-0TH. | The value divided by 100 is ℃, and the measurement range is -20℃~+60℃.
40345 | 30345 | 344 | 158 | 40031 | 30031 | 30 | 1E | 03, 04 | R | Uint16 | Environment humidity. [Note] Use with expansion module iXN-0TH. | The value divided by 100 is %, and the measurement range is 10%~95%.
40346 | 30346 | 345 | 159 | 40032 | 30032 | 31 | 1F | 03, 04 | R | Uint16 | CO concentration. [Note] Use with expansion module iXN-1CX. | The value is ppm, and measuring range: 0~1000 ppm.
40347 | 30347 | 346 | 15A | 40033 | 30033 | 32 | 20 | 03, 04 | R | Uint16 | Vibration MEAN X. [Note] Use with expansion module iXN-2VB3. Vibration MEAN. [Note] Use with expansion module iXN-2VB1. | The value divided by 100 is g, and the measurement range is 0~8g.
40348 | 30348 | 347 | 15B | 40034 | 30034 | 33 | 21 | 03, 04 | R | Uint16 | Vibration MEAN Y. [Note] Use with expansion module iXN-2VB3. Vibration RMS. [Note] Use with expansion module iXN-2VB1
40349 | 30349 | 348 | 15C | 40035 | 30035 | 34 | 22 | 03, 04 | R | Uint16 | Vibration MEAN Z. [Note] Use with expansion module iXN-2VB3. Vibration MAX. [Note] Use with expansion module iXN-2VB1
40350 | 30350 | 349 | 15D | 40036 | 30036 | 35 | 23 | 03, 04 | R | Uint16 | Vibration RMS X. [Note] Use with expansion module iXN-2VB3. | The value divided by 100 is g, and the measurement range is 0~8g.
40351 | 30351 | 350 | 15E | 40037 | 30037 | 36 | 24 | 03, 04 | R | Uint16 | Vibration RMS Y. [Note] Use with expansion module iXN-2VB3.
40352 | 30352 | 351 | 15F | 40038 | 30038 | 37 | 25 | 03, 04 | R | Uint16 | Vibration RMS Z. [Note] Use with expansion module iXN-2VB3.
40353 | 30353 | 352 | 160 | 40039 | 30039 | 38 | 26 | 03, 04 | R | Uint16 | Vibration MAX X. [Note] Use with expansion module iXN-2VB3. | The value divided by 100 is g, and the measurement range is 0~8g.
40354 | 30354 | 353 | 161 | 40040 | 30040 | 39 | 27 | 03, 04 | R | Uint16 | Vibration MAX Y. [Note] Use with expansion module iXN-2VB3.
40355 | 30355 | 354 | 162 | 40041 | 30041 | 40 | 28 | 03, 04 | R | Uint16 | Vibration MAX Z. [Note] Use with expansion module iXN-2VB3.
40356 | 30356 | 355 | 163 | 40042 | 30042 | 41 | 29 | 03, 04 | R | Uint16 | Vibration VECT. [Note] Use with expansion module iXN-2VB3. | The value divided by 100 is g, and the measurement range is 0~8g.
40357 | 30357 | 356 | 164 | 40043 | 30043 | 42 | 2A | - | - | - | - | -
40358 | 30358 | 357 | 165 | 40044 | 30044 | 43 | 2B
40359 | 30359 | 358 | 166 | 40045 | 30045 | 44 | 2C
40360 | 30360 | 359 | 167 | 40046 | 30046 | 45 | 2D
40361 | 30361 | 360 | 168 | 40047 | 30047 | 46 | 2E
40362 | 30362 | 361 | 169 | 40048 | 30048 | 47 | 2F
40363 | 30363 | 362 | 16A | 40049 | 30049 | 48 | 30
40364 | 30364 | 363 | 16B | 40050 | 30050 | 49 | 31
40365 | 30365 | 364 | 16C | 40051 | 30051 | 50 | 32

## Sensor Module Code
Code | Module name | Sensor type | Power supply type | Battery Type | Charging type | Can be expanded?
141 (0x8D) | iWSN-100X | (Connect to expansion module) | Rechargeable Battery x 1 | 14500 (800mAh) | CT or DC+3V | Yes
142 (0x8E) | iWSN-101X | Thermistor x 1

## Expansion Module Code
Code | Module name | Type | Support Module
33 (0x21) | iXN-0TH | Temperature and Humidity x 1 | iWSN-10xX
34 (0x22) | iXN-0VC | TVOC/CO2 x 1
35 (0x23) | iXN-1CX | CO x 1
38 (0x26) | iXN-2VB1 | Vibration (single axis) x 1
39 (0x27) | iXN-2VB3 | Vibration (three axes) x 1
255 (0xFF) | No expansion module connected | - | -

## iWSN Sensor資料_機台差異測試用(100ms) (hidden)
↓輸入站號1~15可計算資料位址
Sensor 站號
1
|  |  |  | Sensor型號 |  |  |  |  | Sensor型號
|  |  |  | 1V6C (24 words) |  |  |  |  | 1V6C (10 words)
Base1 位址 (Dec) | Base1 位址 (Dec) | Base0 位址 (Dec) | Base0 位址 (Hex) | 命令碼 | 屬性 | 資料型態 | 說明 | 備註 | 命令碼 | 屬性 | 資料型態 | 說明 | 備註
40257 | 30257 | 256 | 100 | 03, 04 | R | Uint16 | 第0筆量測資料 | - | 03, 04 | R | Uint16 | 第0筆量測資料 | -
40258 | 30258 | 257 | 101 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40259 | 30259 | 258 | 102 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40260 | 30260 | 259 | 103 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40261 | 30261 | 260 | 104 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40262 | 30262 | 261 | 105 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40263 | 30263 | 262 | 106 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40264 | 30264 | 263 | 107 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40265 | 30265 | 264 | 108 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40266 | 30266 | 265 | 109 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40267 | 30267 | 266 | 10A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第1筆量測資料 | -
40268 | 30268 | 267 | 10B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40269 | 30269 | 268 | 10C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40270 | 30270 | 269 | 10D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40271 | 30271 | 270 | 10E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40272 | 30272 | 271 | 10F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40273 | 30273 | 272 | 110 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40274 | 30274 | 273 | 111 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40275 | 30275 | 274 | 112 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40276 | 30276 | 275 | 113 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40277 | 30277 | 276 | 114 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第2筆量測資料 | -
40278 | 30278 | 277 | 115 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40279 | 30279 | 278 | 116 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40280 | 30280 | 279 | 117 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40281 | 30281 | 280 | 118 | 03, 04 | R | Uint16 | 第1筆量測資料 | - | 03, 04 | R | Uint16
40282 | 30282 | 281 | 119 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40283 | 30283 | 282 | 11A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40284 | 30284 | 283 | 11B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40285 | 30285 | 284 | 11C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40286 | 30286 | 285 | 11D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40287 | 30287 | 286 | 11E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第3筆量測資料 | -
40288 | 30288 | 287 | 11F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40289 | 30289 | 288 | 120 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40290 | 30290 | 289 | 121 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40291 | 30291 | 290 | 122 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40292 | 30292 | 291 | 123 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40293 | 30293 | 292 | 124 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40294 | 30294 | 293 | 125 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40295 | 30295 | 294 | 126 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40296 | 30296 | 295 | 127 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40297 | 30297 | 296 | 128 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第4筆量測資料 | -
40298 | 30298 | 297 | 129 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40299 | 30299 | 298 | 12A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40300 | 30300 | 299 | 12B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40301 | 30301 | 300 | 12C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40302 | 30302 | 301 | 12D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40303 | 30303 | 302 | 12E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40304 | 30304 | 303 | 12F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40305 | 30305 | 304 | 130 | 03, 04 | R | Uint16 | 第2筆量測資料 | - | 03, 04 | R | Uint16
40306 | 30306 | 305 | 131 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40307 | 30307 | 306 | 132 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第5筆量測資料 | -
40308 | 30308 | 307 | 133 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40309 | 30309 | 308 | 134 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40310 | 30310 | 309 | 135 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40311 | 30311 | 310 | 136 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40312 | 30312 | 311 | 137 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40313 | 30313 | 312 | 138 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40314 | 30314 | 313 | 139 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40315 | 30315 | 314 | 13A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40316 | 30316 | 315 | 13B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40317 | 30317 | 316 | 13C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第6筆量測資料 | -
40318 | 30318 | 317 | 13D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40319 | 30319 | 318 | 13E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40320 | 30320 | 319 | 13F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40321 | 30321 | 320 | 140 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40322 | 30322 | 321 | 141 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40323 | 30323 | 322 | 142 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40324 | 30324 | 323 | 143 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40325 | 30325 | 324 | 144 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40326 | 30326 | 325 | 145 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40327 | 30327 | 326 | 146 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第7筆量測資料 | -
40328 | 30328 | 327 | 147 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40329 | 30329 | 328 | 148 | 03, 04 | R | Uint16 | 第3筆量測資料 | - | 03, 04 | R | Uint16
40330 | 30330 | 329 | 149 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40331 | 30331 | 330 | 14A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40332 | 30332 | 331 | 14B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40333 | 30333 | 332 | 14C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40334 | 30334 | 333 | 14D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40335 | 30335 | 334 | 14E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40336 | 30336 | 335 | 14F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40337 | 30337 | 336 | 150 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第8筆量測資料 | -
40338 | 30338 | 337 | 151 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40339 | 30339 | 338 | 152 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40340 | 30340 | 339 | 153 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40341 | 30341 | 340 | 154 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40342 | 30342 | 341 | 155 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40343 | 30343 | 342 | 156 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40344 | 30344 | 343 | 157 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40345 | 30345 | 344 | 158 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40346 | 30346 | 345 | 159 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40347 | 30347 | 346 | 15A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第9筆量測資料 | -
40348 | 30348 | 347 | 15B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40349 | 30349 | 348 | 15C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40350 | 30350 | 349 | 15D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40351 | 30351 | 350 | 15E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40352 | 30352 | 351 | 15F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40353 | 30353 | 352 | 160 | 03, 04 | R | Uint16 | 第4筆量測資料 | - | 03, 04 | R | Uint16
40354 | 30354 | 353 | 161 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40355 | 30355 | 354 | 162 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40356 | 30356 | 355 | 163 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40357 | 30357 | 356 | 164 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第10筆量測資料 | -
40358 | 30358 | 357 | 165 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40359 | 30359 | 358 | 166 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40360 | 30360 | 359 | 167 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40361 | 30361 | 360 | 168 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40362 | 30362 | 361 | 169 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40363 | 30363 | 362 | 16A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40364 | 30364 | 363 | 16B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40365 | 30365 | 364 | 16C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40366 | 30366 | 365 | 16D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40367 | 30367 | 366 | 16E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第11筆量測資料 | -
40368 | 30368 | 367 | 16F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40369 | 30369 | 368 | 170 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40370 | 30370 | 369 | 171 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40371 | 30371 | 370 | 172 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40372 | 30372 | 371 | 173 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40373 | 30373 | 372 | 174 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40374 | 30374 | 373 | 175 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40375 | 30375 | 374 | 176 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40376 | 30376 | 375 | 177 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40377 | 30377 | 376 | 178 | 03, 04 | R | Uint16 | 第5筆量測資料 | - | 03, 04 | R | Uint16 | 第12筆量測資料 | -
40378 | 30378 | 377 | 179 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40379 | 30379 | 378 | 17A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40380 | 30380 | 379 | 17B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40381 | 30381 | 380 | 17C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40382 | 30382 | 381 | 17D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40383 | 30383 | 382 | 17E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40384 | 30384 | 383 | 17F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40385 | 30385 | 384 | 180 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40386 | 30386 | 385 | 181 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40387 | 30387 | 386 | 182 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第13筆量測資料 | -
40388 | 30388 | 387 | 183 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40389 | 30389 | 388 | 184 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40390 | 30390 | 389 | 185 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40391 | 30391 | 390 | 186 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40392 | 30392 | 391 | 187 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40393 | 30393 | 392 | 188 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40394 | 30394 | 393 | 189 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40395 | 30395 | 394 | 18A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40396 | 30396 | 395 | 18B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40397 | 30397 | 396 | 18C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第14筆量測資料 | -
40398 | 30398 | 397 | 18D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40399 | 30399 | 398 | 18E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40400 | 30400 | 399 | 18F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40401 | 30401 | 400 | 190 | 03, 04 | R | Uint16 | 第6筆量測資料 | - | 03, 04 | R | Uint16
40402 | 30402 | 401 | 191 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40403 | 30403 | 402 | 192 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40404 | 30404 | 403 | 193 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40405 | 30405 | 404 | 194 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40406 | 30406 | 405 | 195 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40407 | 30407 | 406 | 196 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第15筆量測資料 | -
40408 | 30408 | 407 | 197 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40409 | 30409 | 408 | 198 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40410 | 30410 | 409 | 199 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40411 | 30411 | 410 | 19A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40412 | 30412 | 411 | 19B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40413 | 30413 | 412 | 19C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40414 | 30414 | 413 | 19D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40415 | 30415 | 414 | 19E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40416 | 30416 | 415 | 19F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40417 | 30417 | 416 | 1A0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第16筆量測資料 | -
40418 | 30418 | 417 | 1A1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40419 | 30419 | 418 | 1A2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40420 | 30420 | 419 | 1A3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40421 | 30421 | 420 | 1A4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40422 | 30422 | 421 | 1A5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40423 | 30423 | 422 | 1A6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40424 | 30424 | 423 | 1A7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40425 | 30425 | 424 | 1A8 | 03, 04 | R | Uint16 | 第7筆量測資料 | - | 03, 04 | R | Uint16
40426 | 30426 | 425 | 1A9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40427 | 30427 | 426 | 1AA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第17筆量測資料 | -
40428 | 30428 | 427 | 1AB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40429 | 30429 | 428 | 1AC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40430 | 30430 | 429 | 1AD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40431 | 30431 | 430 | 1AE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40432 | 30432 | 431 | 1AF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40433 | 30433 | 432 | 1B0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40434 | 30434 | 433 | 1B1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40435 | 30435 | 434 | 1B2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40436 | 30436 | 435 | 1B3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40437 | 30437 | 436 | 1B4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第18筆量測資料 | -
40438 | 30438 | 437 | 1B5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40439 | 30439 | 438 | 1B6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40440 | 30440 | 439 | 1B7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40441 | 30441 | 440 | 1B8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40442 | 30442 | 441 | 1B9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40443 | 30443 | 442 | 1BA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40444 | 30444 | 443 | 1BB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40445 | 30445 | 444 | 1BC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40446 | 30446 | 445 | 1BD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40447 | 30447 | 446 | 1BE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | 第19筆量測資料 | -
40448 | 30448 | 447 | 1BF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40449 | 30449 | 448 | 1C0 | 03, 04 | R | Uint16 | 第8筆量測資料 | - | 03, 04 | R | Uint16
40450 | 30450 | 449 | 1C1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40451 | 30451 | 450 | 1C2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40452 | 30452 | 451 | 1C3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40453 | 30453 | 452 | 1C4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40454 | 30454 | 453 | 1C5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40455 | 30455 | 454 | 1C6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40456 | 30456 | 455 | 1C7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40457 | 30457 | 456 | 1C8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16 | - | -
40458 | 30458 | 457 | 1C9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40459 | 30459 | 458 | 1CA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40460 | 30460 | 459 | 1CB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40461 | 30461 | 460 | 1CC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40462 | 30462 | 461 | 1CD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40463 | 30463 | 462 | 1CE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40464 | 30464 | 463 | 1CF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40465 | 30465 | 464 | 1D0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40466 | 30466 | 465 | 1D1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40467 | 30467 | 466 | 1D2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40468 | 30468 | 467 | 1D3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40469 | 30469 | 468 | 1D4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40470 | 30470 | 469 | 1D5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40471 | 30471 | 470 | 1D6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40472 | 30472 | 471 | 1D7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40473 | 30473 | 472 | 1D8 | 03, 04 | R | Uint16 | 第9筆量測資料 | - | 03, 04 | R | Uint16
40474 | 30474 | 473 | 1D9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40475 | 30475 | 474 | 1DA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40476 | 30476 | 475 | 1DB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40477 | 30477 | 476 | 1DC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40478 | 30478 | 477 | 1DD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40479 | 30479 | 478 | 1DE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40480 | 30480 | 479 | 1DF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40481 | 30481 | 480 | 1E0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40482 | 30482 | 481 | 1E1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40483 | 30483 | 482 | 1E2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40484 | 30484 | 483 | 1E3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40485 | 30485 | 484 | 1E4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40486 | 30486 | 485 | 1E5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40487 | 30487 | 486 | 1E6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40488 | 30488 | 487 | 1E7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40489 | 30489 | 488 | 1E8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40490 | 30490 | 489 | 1E9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40491 | 30491 | 490 | 1EA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40492 | 30492 | 491 | 1EB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40493 | 30493 | 492 | 1EC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40494 | 30494 | 493 | 1ED | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40495 | 30495 | 494 | 1EE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40496 | 30496 | 495 | 1EF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40497 | 30497 | 496 | 1F0 | 03, 04 | R | Uint16 | 第10筆量測資料 | - | 03, 04 | R | Uint16
40498 | 30498 | 497 | 1F1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40499 | 30499 | 498 | 1F2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40500 | 30500 | 499 | 1F3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40501 | 30501 | 500 | 1F4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40502 | 30502 | 501 | 1F5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40503 | 30503 | 502 | 1F6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40504 | 30504 | 503 | 1F7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40505 | 30505 | 504 | 1F8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40506 | 30506 | 505 | 1F9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40507 | 30507 | 506 | 1FA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40508 | 30508 | 507 | 1FB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40509 | 30509 | 508 | 1FC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40510 | 30510 | 509 | 1FD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40511 | 30511 | 510 | 1FE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40512 | 30512 | 511 | 1FF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40513 | 30513 | 512 | 200 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40514 | 30514 | 513 | 201 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40515 | 30515 | 514 | 202 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40516 | 30516 | 515 | 203 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40517 | 30517 | 516 | 204 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40518 | 30518 | 517 | 205 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40519 | 30519 | 518 | 206 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40520 | 30520 | 519 | 207 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40521 | 30521 | 520 | 208 | 03, 04 | R | Uint16 | 第11筆量測資料 | - | 03, 04 | R | Uint16
40522 | 30522 | 521 | 209 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40523 | 30523 | 522 | 20A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40524 | 30524 | 523 | 20B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40525 | 30525 | 524 | 20C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40526 | 30526 | 525 | 20D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40527 | 30527 | 526 | 20E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40528 | 30528 | 527 | 20F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40529 | 30529 | 528 | 210 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40530 | 30530 | 529 | 211 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40531 | 30531 | 530 | 212 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40532 | 30532 | 531 | 213 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40533 | 30533 | 532 | 214 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40534 | 30534 | 533 | 215 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40535 | 30535 | 534 | 216 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40536 | 30536 | 535 | 217 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40537 | 30537 | 536 | 218 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40538 | 30538 | 537 | 219 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40539 | 30539 | 538 | 21A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40540 | 30540 | 539 | 21B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40541 | 30541 | 540 | 21C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40542 | 30542 | 541 | 21D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40543 | 30543 | 542 | 21E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40544 | 30544 | 543 | 21F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40545 | 30545 | 544 | 220 | 03, 04 | R | Uint16 | 第12筆量測資料 | - | 03, 04 | R | Uint16
40546 | 30546 | 545 | 221 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40547 | 30547 | 546 | 222 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40548 | 30548 | 547 | 223 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40549 | 30549 | 548 | 224 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40550 | 30550 | 549 | 225 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40551 | 30551 | 550 | 226 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40552 | 30552 | 551 | 227 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40553 | 30553 | 552 | 228 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40554 | 30554 | 553 | 229 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40555 | 30555 | 554 | 22A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40556 | 30556 | 555 | 22B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40557 | 30557 | 556 | 22C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40558 | 30558 | 557 | 22D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40559 | 30559 | 558 | 22E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40560 | 30560 | 559 | 22F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40561 | 30561 | 560 | 230 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40562 | 30562 | 561 | 231 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40563 | 30563 | 562 | 232 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40564 | 30564 | 563 | 233 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40565 | 30565 | 564 | 234 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40566 | 30566 | 565 | 235 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40567 | 30567 | 566 | 236 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40568 | 30568 | 567 | 237 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40569 | 30569 | 568 | 238 | 03, 04 | R | Uint16 | 第13筆量測資料 | - | 03, 04 | R | Uint16
40570 | 30570 | 569 | 239 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40571 | 30571 | 570 | 23A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40572 | 30572 | 571 | 23B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40573 | 30573 | 572 | 23C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40574 | 30574 | 573 | 23D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40575 | 30575 | 574 | 23E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40576 | 30576 | 575 | 23F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40577 | 30577 | 576 | 240 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40578 | 30578 | 577 | 241 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40579 | 30579 | 578 | 242 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40580 | 30580 | 579 | 243 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40581 | 30581 | 580 | 244 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40582 | 30582 | 581 | 245 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40583 | 30583 | 582 | 246 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40584 | 30584 | 583 | 247 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40585 | 30585 | 584 | 248 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40586 | 30586 | 585 | 249 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40587 | 30587 | 586 | 24A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40588 | 30588 | 587 | 24B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40589 | 30589 | 588 | 24C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40590 | 30590 | 589 | 24D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40591 | 30591 | 590 | 24E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40592 | 30592 | 591 | 24F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40593 | 30593 | 592 | 250 | 03, 04 | R | Uint16 | 第14筆量測資料 | - | 03, 04 | R | Uint16
40594 | 30594 | 593 | 251 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40595 | 30595 | 594 | 252 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40596 | 30596 | 595 | 253 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40597 | 30597 | 596 | 254 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40598 | 30598 | 597 | 255 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40599 | 30599 | 598 | 256 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40600 | 30600 | 599 | 257 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40601 | 30601 | 600 | 258 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40602 | 30602 | 601 | 259 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40603 | 30603 | 602 | 25A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40604 | 30604 | 603 | 25B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40605 | 30605 | 604 | 25C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40606 | 30606 | 605 | 25D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40607 | 30607 | 606 | 25E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40608 | 30608 | 607 | 25F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40609 | 30609 | 608 | 260 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40610 | 30610 | 609 | 261 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40611 | 30611 | 610 | 262 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40612 | 30612 | 611 | 263 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40613 | 30613 | 612 | 264 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40614 | 30614 | 613 | 265 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40615 | 30615 | 614 | 266 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40616 | 30616 | 615 | 267 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40617 | 30617 | 616 | 268 | 03, 04 | R | Uint16 | 第15筆量測資料 | - | 03, 04 | R | Uint16
40618 | 30618 | 617 | 269 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40619 | 30619 | 618 | 26A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40620 | 30620 | 619 | 26B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40621 | 30621 | 620 | 26C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40622 | 30622 | 621 | 26D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40623 | 30623 | 622 | 26E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40624 | 30624 | 623 | 26F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40625 | 30625 | 624 | 270 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40626 | 30626 | 625 | 271 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40627 | 30627 | 626 | 272 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40628 | 30628 | 627 | 273 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40629 | 30629 | 628 | 274 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40630 | 30630 | 629 | 275 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40631 | 30631 | 630 | 276 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40632 | 30632 | 631 | 277 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40633 | 30633 | 632 | 278 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40634 | 30634 | 633 | 279 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40635 | 30635 | 634 | 27A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40636 | 30636 | 635 | 27B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40637 | 30637 | 636 | 27C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40638 | 30638 | 637 | 27D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40639 | 30639 | 638 | 27E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40640 | 30640 | 639 | 27F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40641 | 30641 | 640 | 280 | 03, 04 | R | Uint16 | 第16筆量測資料 | - | 03, 04 | R | Uint16
40642 | 30642 | 641 | 281 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40643 | 30643 | 642 | 282 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40644 | 30644 | 643 | 283 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40645 | 30645 | 644 | 284 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40646 | 30646 | 645 | 285 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40647 | 30647 | 646 | 286 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40648 | 30648 | 647 | 287 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40649 | 30649 | 648 | 288 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40650 | 30650 | 649 | 289 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40651 | 30651 | 650 | 28A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40652 | 30652 | 651 | 28B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40653 | 30653 | 652 | 28C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40654 | 30654 | 653 | 28D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40655 | 30655 | 654 | 28E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40656 | 30656 | 655 | 28F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40657 | 30657 | 656 | 290 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40658 | 30658 | 657 | 291 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40659 | 30659 | 658 | 292 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40660 | 30660 | 659 | 293 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40661 | 30661 | 660 | 294 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40662 | 30662 | 661 | 295 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40663 | 30663 | 662 | 296 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40664 | 30664 | 663 | 297 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40665 | 30665 | 664 | 298 | 03, 04 | R | Uint16 | 第17筆量測資料 | - | 03, 04 | R | Uint16
40666 | 30666 | 665 | 299 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40667 | 30667 | 666 | 29A | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40668 | 30668 | 667 | 29B | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40669 | 30669 | 668 | 29C | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40670 | 30670 | 669 | 29D | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40671 | 30671 | 670 | 29E | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40672 | 30672 | 671 | 29F | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40673 | 30673 | 672 | 2A0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40674 | 30674 | 673 | 2A1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40675 | 30675 | 674 | 2A2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40676 | 30676 | 675 | 2A3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40677 | 30677 | 676 | 2A4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40678 | 30678 | 677 | 2A5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40679 | 30679 | 678 | 2A6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40680 | 30680 | 679 | 2A7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40681 | 30681 | 680 | 2A8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40682 | 30682 | 681 | 2A9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40683 | 30683 | 682 | 2AA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40684 | 30684 | 683 | 2AB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40685 | 30685 | 684 | 2AC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40686 | 30686 | 685 | 2AD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40687 | 30687 | 686 | 2AE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40688 | 30688 | 687 | 2AF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40689 | 30689 | 688 | 2B0 | 03, 04 | R | Uint16 | 第18筆量測資料 | - | 03, 04 | R | Uint16
40690 | 30690 | 689 | 2B1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40691 | 30691 | 690 | 2B2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40692 | 30692 | 691 | 2B3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40693 | 30693 | 692 | 2B4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40694 | 30694 | 693 | 2B5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40695 | 30695 | 694 | 2B6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40696 | 30696 | 695 | 2B7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40697 | 30697 | 696 | 2B8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40698 | 30698 | 697 | 2B9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40699 | 30699 | 698 | 2BA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40700 | 30700 | 699 | 2BB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40701 | 30701 | 700 | 2BC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40702 | 30702 | 701 | 2BD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40703 | 30703 | 702 | 2BE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40704 | 30704 | 703 | 2BF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40705 | 30705 | 704 | 2C0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40706 | 30706 | 705 | 2C1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40707 | 30707 | 706 | 2C2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40708 | 30708 | 707 | 2C3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40709 | 30709 | 708 | 2C4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40710 | 30710 | 709 | 2C5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40711 | 30711 | 710 | 2C6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40712 | 30712 | 711 | 2C7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40713 | 30713 | 712 | 2C8 | 03, 04 | R | Uint16 | 第19筆量測資料 | - | 03, 04 | R | Uint16
40714 | 30714 | 713 | 2C9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40715 | 30715 | 714 | 2CA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40716 | 30716 | 715 | 2CB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40717 | 30717 | 716 | 2CC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40718 | 30718 | 717 | 2CD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40719 | 30719 | 718 | 2CE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40720 | 30720 | 719 | 2CF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40721 | 30721 | 720 | 2D0 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40722 | 30722 | 721 | 2D1 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40723 | 30723 | 722 | 2D2 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40724 | 30724 | 723 | 2D3 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40725 | 30725 | 724 | 2D4 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40726 | 30726 | 725 | 2D5 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40727 | 30727 | 726 | 2D6 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40728 | 30728 | 727 | 2D7 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40729 | 30729 | 728 | 2D8 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40730 | 30730 | 729 | 2D9 | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40731 | 30731 | 730 | 2DA | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40732 | 30732 | 731 | 2DB | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40733 | 30733 | 732 | 2DC | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40734 | 30734 | 733 | 2DD | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40735 | 30735 | 734 | 2DE | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40736 | 30736 | 735 | 2DF | 03, 04 | R | Uint16 |  |  | 03, 04 | R | Uint16
40737 | 30737 | 736 | 2E0 | 03, 04 | R | Uint16 | 當前封包存放之索引值 | - | 03, 04 | R | Uint16 | 當前封包存放之索引值 | -
40738 | 30738 | 737 | 2E1 | 03, 04 | R | Uint16 | 當前封包存放之起始位址 | - | 03, 04 | R | Uint16 | 當前封包存放之起始位址 | -
40739 | 30739 | 738 | 2E2 | 03, 04 | R | Uint16 | 當前封包存放在FRAM之起始位址 | - | 03, 04 | R | Uint16 | 當前封包存放在FRAM之起始位址 | -