Watchdog Application for I-7K / I-87K I/O modules

For distributed slave I/O application, host application always sends commands to remote I/O modules via communication bus like RS-485 or Ethernet.

If communication between host application and remote I/O modules are broken or interrupted by unknown reasons, the remote I/O modules will be out of control.

If remote I/O modules include digital output or analog output modules, in such application, if communication status is out of control, it will be dangerous in most applications.

For ICP DAS I-7K / I-87K digital output and analog output modules are embedded with host watchdog function and can set safe values if host watchdog status timeout.

I-7K/ I-87K I/O 模組看門狗應用

在主從式架構的分散式控制系統中, 通常由主機程式透過RS-485或Ethernet網路通訊介面, 發出命令給遠端模組. 如果主機與遠端輸出/輸入模組之間的連線硬體設施發生故障, 或電源故障等其他原因導致主機送出不正確的命令, 有可能會讓模組輸出異常的訊號造成系統的損壞.

因此, 在分散式通訊系統中, 需要加入看門狗機制, 提高系統的安全性. 當通訊發生問題時, 看門狗進入警戒狀態, 所有的輸出通道包含數位輸出與類比輸出, 必須將輸出通道的訊號切換到安全狀態或安全值. 看門狗警戒期間, 所有模組不會接受輸出命令. 等主機恢復正常通信, 清除看門狗警戒狀態後, 輸出通道才能根據收到的命令繼續動作.

Start

Set DO Safe Value (@AA(data)

Set WDT Timeout (~AA31FF)

Loop Function

End

Output DO values (@AA(data)

Refresh WDT timer (~**)

Enable Safe Value (~AA5S)

Set Initial DO Value (@AA(data)

Read WDT Status (~AA0)

WDT Timeout Procedure

WDT Timeout (!AA04)

Normal (!AA00)

Note 1

Note 2

Note 3

Note 4

Set WDT Timeout (~AA31FF)

Loop Function

End

Output DO values (@AA(data)

Refresh WDT timer (~**)

Set Normal DO Value (@AA(data)

Read WDT Status (~AA0)

WDT Timeout (!AA04)

Normal (!AA00)

WDT Timeout Procedure

Check Communication Status

Clear WDT Flag (~AA1)

Note 5

Note 6

8通道數位輸出模組I-87064的控制命令請參考網頁http://ftp.icpdas.com/pub/cd/8000cd/napdos/dcon/io_module/87k/dio/87064/dcon_87k/87064_dcon_87k.htm

以下以I-87064, 位址為1 為例

Note 1: 
1: @01FF將8通道輸出值設定為1

2: ~015S 將目前DO狀態設定為安全值.

3: 使用~015S之後, 需要再送一次輸出命令將所有輸出通道設定成初始狀態

例如: @0100將所有通道輸出值設定為0

Note 2: How to configure host watchdog timeout value and enable host watchdog: The WDT timeout value can be from 0~ 25.5 sec ( I think 0 second is no use for real application)
 you can use command ~0131FF to enable WDT and set WDT timeout value as 
25.5 sec ( FF is 255 and 25.5 = 255/10)
 now, you have enable WDT function and start up WDT timer
 use ~012 can check the WDT configuration as !001FF

Note 3: How to reset watchdog timer.
1. To Reset WDT timer by using broadcast command ~**

~** command will not echo any response and we have add more than two characters delay time between ~** and next command

2. Because we set WDT timeout value as 25.5 second, I-87064 must receive 
~** within 25.5 second or it will enter WDT timeout status and DO will enter 
safe value. Normally, I can send this broadcast command at about 25/2 = 12 second 
interval to reset WDT timer.

3.  In IPAC-8000, WinPAC, XPAC-CE6, XPAC-XPE or LinPAC-8000 system, we have to use API to ChangeToSolt before you want to send any command to I-87K modules include broadcast command ~**.
   
Note 4: How to check if host watchdog timeout.

1. If WDT timeout, the DO power LED will be flash status and any output 
command will be failed.

When I-87084 DO modules enter safe value, any output command will will get ?01 response from I-87064, this is the most be frequently asked output problem for Digital output modules and Analog output modules.

2. Polling WDT status to make sure if host watchdog timer timeout
 we can use ~010 to read module WDT status, if it is normal the response 
will be !0100, if WDT timeout, the response will be !0104
 
Note 5: Check communication status if host watchdog timeout.

1. When applications enter host watchdog timeout state, it means there may have communication problems between host application and remote I/O modules.

2. Check the communication line if it was loose at terminal board.

3. Make sure the communication problems have been removed before go to next step, if there still exist some communication problems in system, the communication will be unstable and often enter safe value.

Note 6: How to recovered from safe value.
1: Clear WDT Timeout Flag
When WDT timeout, we have to use ~011 to clear WDT timeout flag, after 
we clear WDT timeout flag, output module can be controlled again.
2. Because system had been entered safe value state, applications have to define the output state when we clear watchdog flag.
3: To enable WDT status again, when I-7K /I-87K output module's WDT timeout, the WDT enable flag will be disabled, to use command ~012 can check the status, we have to use ~0131FF command to enable the WDT again.